# Compact air handling unit with heat recovery and integrated controls

Compact air handling unit with highly efficient heat recovery and integrated microprocessor controls, factory tested and started-up.

Available in the versions:

F - Flat unit for ceiling mounting

**Housing**

Frameless, double wall galvanized sheet steel housing with anti-fingerprint coating. The mineral wool used as heat and sound insulation is non-flammable according to building material class DIN EN 13501-1, class A1. Depending on the device version, insulation boards with a density of 110kg/m³ of the WLG 040 in a thickness of up to 50mm are used. The large doors of the V and H variants are equipped with hinges and lockable locks as standard, and the operating doors of the F variants can be removed. All installation components are easily accessible from the operator side. All floor and side panels are always hygienically sealed against each other

All devices (except for the F variants) are delivered with a retractable base frame. The variant H is also suitable for outdoor installation with optionally available accessories. The housings are smooth inside and easy to clean.

Housing quality EN 1886

Mechanical stability: D2

Housing leakage over pressure (+700Pa): L2

Filter bypass leakage: F9

Heat transfer class: T3

Thermal bridging factor: TB3

Material class EN 13501-1 housing: A1

Consistent high quality assurance is demonstrated by the certification according to ISO 9001:2015.

Supplier information: ruck Ventilatoren GmbH

Max-Planck-Straße 5

97944 Boxberg

Tel. 07930-9211300

www.ruck.eu

**Fans (MES)**

Direct drive single suction fans with backward curved high-performance radial impellers, mounted on an EC external rotor motor with integrated control electronics. Motor impeller statically and dynamically balanced in two planes, according to DIN ISO 1940, balance quality G 6.3. The EC external rotor motor exceeds efficiency class IE4, magnets without use of rare earths, maintenance-free ball bearings with long-term lubrication, theoretically nominal life of at least 40,000 operating hours. Fan can be used on all conventional power supply networks with unchanged air flow. Integrated electronics, low-noise commutation logic; 100% speed controllable. The fan units are extractable, the cables with plug connection can be separated without tools for maintenance purposes.

**Heat recovery (Akku)**

High-performance heat exchanger with up to 93% heat and cold recovery to cover the ventilation heat demand in statically heated rooms.

The resulting condensate is immediately absorbed by the passing air after switching, up to 70% moisture recovery is possible. Additional condensate trays are not needed. The angular geometry of the storage mass allows the full utilization of the device cross-section and thus reduces the pressure losses. The storage mass heat exchanger works even at low outside temperatures without power reduction by antifreeze systems. The countercurrent flow of the air causes a self-cleaning effect of dry impurities. Very good hygienic properties of the heat exchanger due to no substances exchange on the heat exchanger surface made of aluminum. The storage masses can be removed for cleaning. The year-round high efficiencies make the use of a after heater to cover the ventilation heat demand unnecessary. Including flap system, tightness class 2, for switching the air flows.

**Panel filter**

Compact panel filters with long service life, easy filter change by quick release frame.

Supply air filter F7 according to EN779:2012 (new, ISO ePM2.5 ≥ 70%), consisting of an abrasion-resistant and water-repellent polypropylene fiber, polystyrene frame, fully incinerable.

Extract air filter M5 according to EN779:2012 (new ISO ePM10 ≥ 65%), filter frame made of polystyrene extruded profiles, fully incinerable, synthetic fiber fleece with intrinsically stiff folds and additional spacers made of plastic.

The high filter-tightness class is achieved by a quick-release device that acts on the filter frame on an EPDM crown seal. It is structurally ensured that the operating door can only be closed when the filter is clamped.

**Controls**

Control cabinet with controls components and all required field devices are integrated in the base unit.

Integrated CONSTANT AIR VOLUME system with nozzle pressure measuring points on both fans. The control system compensates for the outside air-dependent density change of the air. As a result, regardless of the fan position, a constant year-round volume flow in the supply air and extract air on the room side is ensured. The energy savings for fans and reheating are up to 15%.

Each of the three supply air and exhaust air streams can be steplessly adjusted. Via the remote control unit the volume flows can be set in a user-friendly manner in three stages. Combined PV constant volume flow / constant pressure control for VAV systems in non-residential buildings.

In the case of an air volume zone control of several volume flow controllers, the control ensures a constant inlet pressure in the supply air with a traced exhaust air volume flow. The control mode ensures the same supply air and exhaust air volume flows, even in case of zone control, and prevents underpressure or overpressure in the rooms. In addition, unequal volume flows are avoided, which can adversely affect the heat recovery.

Both filters are equipped with differential pressure monitoring. The degree of contamination of the filter is displayed via the remote control unit.

Integrated free building cooling

The integrated controls activates the free cooling of the building in the event of an increased internal heat load during the transition period or on hot summer days. The room is cooled by switching off the heat recovery with cool outside air and without additional energy requirements.

Model: ACCU K 600 F OOJR/L

Device version: indoor installation

Compliance with the regulation (EU) no. 1253/2014

The tendered compact device fulfills the requirements of the ErP Directive 2009/125/EC of the European Parliament for the sector "Non Residential". Both recovery grade of the energy recovery and also the required values for the SFPint are maintained at the below specified operating point.

**Air performance supply air (ErP2018):**

Volumetric flow: 605 m³/h

External pressure loss: 278 Pa

SFP class: SFP2

Specific fan power: 1027 W/(m³/s)

(SFPV SUP according EN 16798-3)

**Heat recovery high efficient switch over reservoirs**

Power: 6 KW

Outdoor air inlet: -12°C/90%rf

Supply air outlet: 17,5 °C

Extract air inlet: 20°C/40%rf

Heat recovery rate ηWRG acc. to EN 308: 92,20 %

Energy efficiency acc. to EN13053: 89,87 %

Pressure drop supply air: 177 Pa

Pressure drop extract air: 196 Pa

**Filter unit outdoor air**

Filter class according to EN 779: F7

Filter class acording to ISO16890: ISO ePM2,5 ≥ 70%

Dimensions: 430/300 mm

Filter surface: 2,91 m²

**Filter unit extract air**

Filter class according to EN 779: M5

Filter class acording to ISO16890: ISO ePM10 ≥ 65%

Dimensions: 430/300 mm

Filter surface: 1,45 m²

**Controls**

DDC, command, control unit and control board are integrated in the housing and wired ready for operation with all pre-assembled field devices. All operating and status parameters can be parameterized via the convenient touch remote control unit with graphic display, via the RUCKVIEW software or the MODBUS communication interface.

Fans functions

• Operating mode V constant volume control

• Operating mode P constant pressure control

• Operating mode PV constant volume / constant pressure control

Temperature control functions

• Operating mode supply air temperature control

• Operating mode extract air temperature control

• Operating mode room air temperature control

• Free cooling via outside air bypass (free night cooling)

• Heat recovery without after heating

• Warm water heating (at PWW version)

• Cooling DX-coil

• Heating warm water and cooling cold water

(at PWW version)

• Heating condenser and cooling DX-coil

(at PWW version)

Monitoring functions:

• Temperature monitoring supply, extract, exhaust, outdoor air

• Frost protection monitoring of the warm water heating coils (at PWW version)

• Air filters monitoring via pressure difference

• Automatic adjustment of ventilation capacity at very low outside temperatures

• Plausibility check of the sensor against cable break

Inputs:

• MODBUS RTU interface

• Motion sensor potential-free contact

• Frost protection thermostat potential-free contact

• Fire detector potential-free contact

• Unit enable, potential-free contact

• Pressure sensor SEN P for P and PV control

• Control input for external volume flow control

• Control input for external CO2, VOC or humidity sensors

Outputs:

• Fan supply air (0-10V)

• Fan extract air (0-10V)

• Valve heating circuit (0-10V and 3-point control) (at PWW version)

• Valve cooling circuit (0-10V and 3-point control)

• Enable cooling device

• Circulation pump heating circuit (at PWW version)

• Fault indication with error code displayed on the remote control unit and potential-free output contact

• Bypass damper (3-point control)

• Outside air damper (open/close or spring return)

• Extract air damper (open/close or spring return)

**Data according to EN 13053/A1:2017**

WRG class: H1

Speed class: V1

Electrical power consumption: P1

**Electrical performance data overall device**

Voltage: 230V 1~

Current: 2,5A

Power consumption: 500 W

**General data**

Insulation thickness 30mm

Conveyed medium temperature: 40°C

Weight: 198kg

Length/width height: 1800/1105/411mm

Duct connection: 400/200mm

**Scope of supply:**

1x ACCU K 600 F OOJR

1x BDT-Touch, remote control unit

1x control cable length10m

1x Installation and operation manual

**Optional accessories:**

**COM2-Option**

Expansion board for connecting several compact devices via Modbus, with switchable terminating resistor and switchable pull-up and pull-down resistor, factory mounted and wired in the compact device

Art.no.: 128549

**SEN P1000**

Differential pressure sensor Measuring range +/- 1000Pa accessories for operating mode P (constant pressure control), 2 pieces necessary (monitoring supply / extract air),

Assembly on site

Art.no.: 126080

**CLIMASET01**

Mounting accessories for pressure devices / pressure sensors, consisting of 2m hose, two measuring nipples with screw flange and screws, temperature resistant up to +70°C

Art.no.: 111314

**SEN CO2-Option**

Combined temperature / CO2 sensor with attractive wall-mounted housing, measurement via long-term stable 2-beam infrared cell, factory mounted and wired in the compact unit

Art.no.: 127338

**SEN RH**

Combined temperature /humidity sensor with attractive wall-mounted housing IP30.

Supply voltage 15…24Vdc. Output 2 x 0-10V

Art.no.: 148636

**SEN RAUCH 01**

Duct smoke sensor IP54 (with WDG IP65) with DIBt certification. Detector type scattering RM3.3. Supply voltage 230 V AC ±10%, 50/60Hz. Relay outputs potential-free.

Art.no.: 148638

**SEN RAUCH 02**

Duct smoke sensor IP54 (with WDG IP65) without DIBt certification. Detector type scattering RM3.3. Supply voltage 230 V AC ±10%, 50/60Hz. Relay outputs potential-free.

Art.no.: 148637

**SEN TEMP**

Duct temperature sensor IP65. NTC 5k, -50...+150°C

Art.no.: 148639

**RUCKVIEW**

The ruckview control system has so far replaced very complex and object-related BUS control systems for ventilation units. With its easy handling, end users can quickly set, operate and manage the ventilation units for the highest level of efficiency. With the ruckview software, up to 30 ruck ventilation units can be monitored and controlled via a PC. Furthermore, all parameters and actual values can be easily read out for the service technician, which greatly simplifies commissioning and maintenance. The included Team Viewer remote monitoring program allows access to your ventilation system via the Internet.

Scope of delivery ruckview software:

• ruckview control software for ruck air handling units with MOD-BUS RTU

• Connection box for MOD-BUS cable

• USB-data cable for connection box

• Remote monitoring software OEM Version

• USB-Stick, user manual

Software requirements

• Operating system Windows XP, Windows Vista, Windows7,

Windows 8, Windows 10

Art.no.: 130247

**Commissioning building management software**

Commissioning of building control technology by factory customer service of ventilation

equipment for a single arrival.

Consisting of:

• Checking the ModBus data line connected to the customer

Expansion boards of the ventilation units

• Installation of the software on an on-site Windows computer of the operator

• Setting the device IDs on the ventilation units

• Setting the required parameters

• Test run of the ventilation units

• Briefing of the operating staff

• Creation of a commissioning protocol with indication of commissioning

settings

**Replacement panel filters**

Supply air filter F7 according to EN779:2012 (new, ISO ePM2.5 ≥ 70%), consisting of an abrasion-resistant and water-repellent polypropylene fiber, polystyrene frame, fully incinerable.

Extract air filter M5 according to EN779:2012 (new ISO ePM10 ≥ 65%), filter frame made of polystyrene extruded profiles, fully incinerable, synthetic fiber fleece with intrinsically stiff folds and additional spacers made of plastic.

LFP60 F7 Art.no.: 140539, 1 piece pro filter change necessary

LFP60 M5 Art.no.: 140538, 1 piece pro filter change necessary

**KWR (extern)**

Cooling is done via a separate cooling module. Single wall housing, round connections DN 250, galvanized sheet steel with anti-fingerprint coating. Revision cover side removable with quick release fasteners as well as pre-punched inlets for medium pipes. Frames and panels made of galvanized sheet steel, tubes and collectors made of copper, fins made of aluminum (0 , 1 - 0.15mm), minimum lamellar spacing 1,8mm. The register is suitable for water, as well as water/glycol mixtures, the test pressure is 18bar, operating pressure max. 16bar.

The cooler module is equipped with a condensate tray made of stainless steel (at least 1.4301), a droplet separator can be dispensed due to the horizontal arrangement of the cooler.

Optional is available a control ball valve dimensioned to the cooler capacity. The setpoint specification is programmed via the control panel of the compact unit (supply air temperature control).

KWR 250 01 (version right) Art.no.: 124065

KWR 250 02 (version left) Art.no.: 124066

**DVR (extern)**

Cooling is done via a separate DX-coil module. Single wall housing, round connections DN 250, galvanized sheet steel with anti-fingerprint coating. Revision cover side removable with quick release fasteners as well as pre-punched inlets for medium pipes.

Sheet steel frames and panels, copper pipes and collectors, aluminum fins (0,1 - 0,15mm), minimum lamellar spacing 2,0mm. With spreader spider for multiple injection, suction via copper collector pipe leading out for solder connection. The test pressure is 55bar, operating pressure max. 41bar and thus suitable for reverse operation.

The cooler module is equipped with a condensate tray made of stainless steel (at least 1.4301), a droplet separator can be dispensed due to the horizontal arrangement of the cooler.

The setpoint specification is programmed via the control panel of the compact unit (supply air temperature control).

DVR 250 01 (version right) Art.no.: 126775

DVR 250 02 (version left) Art.no.: 126776

**RSK…D**

Automatic back draught shutter for pipe installation, housing made of galvanized sheet steel, flaps made of aluminum with EPDM seal.

RSK 250D, DN 250 mm Art.no.: 113488

**VM**

Fast clamps for tube connection, for sound decoupling and sealing. Material galvanized sheet steel, sealing with 5mm neoprene seal, delivery unit 1 pack = 2 pieces

VM 250, DN 250 mm Art.no.: 102651

**SDS**

Tubular silencer, rigid design, galvanized sheet steel jacket, 50mm mineral wool lining

Nominal diameter 250 mm

Outside diameter 412 mm

Length 1050 mm

SDS 250 Art.no.: 102721

**SDF**

Tubular silencer, flexible design, galvanized sheet steel jacket, 50mm mineral wool lining

Nominal diameter 250 mm

Outside diameter 355 mm

Length 1000 mm

SDF 250 Art.no.: 102705

**MAK**

Motor damper for tube installation, for shutting off and throttling the air flow. Ready-to-install butterfly damper, housing and flap made of galvanized sheet steel, flap seal made of EPDM.

Actuator 230V / 50Hz attached to butterfly valve.

MAK 250 01 actuator with spring return Art.no.: 124067

MAK 250 02 actuator open/close 3-point Art.no.: 124068

**UKR**

Transitions rectangular to round connection, material galvanized sheet steel, duct frame PG20, round connection as insertion end

UKR 4020 05 400x200m – d=250mm Art.no.: 140939

**VS – Flexible duct collar**

With standard profile flange P20, galvanized sheet steel, plastic band (PVC)

for structure-borne noise decoupling, Temperature stability to 70 °C

VS4020 Art.no.: 102802