Description:

Centrifugal roof fan with backward curved impeller and vertical discharge. Housing made of weather-resistant aluminum AlMg3 with very low construction height, swing out design. The air outlet is protected by a protection grille against intrusion, birds and other foreign objects. Baseplate of galvanized steel sheet with deep drawn air inlet and preassembled screws for the possibility of connecting pipe flanges and accessories according to DIN 24154 / EN 12 220. The fan has been conceived for easy mounting on roof socket (optional accessory) without the necessity of removing the housing.

The impeller with backward curved blades is fitted on the external rotor of an energy saving, high efficiency EC-motor and together balanced according to the quality class G 6.3 of DIN / ISO 1940, on 2 planes. The drive motor is equipped, for maintenance-free use, with ball bearings with lifetime lubrication, sealed on both sides. The motor protection is provided by a thermal contact integrated into the winding, permanently monitored by the motor electronic. The electrical connection is to be done via the cable lead out through the housing base plate. When necessary, the integrated constant pressure control automatically adjusts the fan speed to adapt to the air capacity. The power switch is integrated into the housing and separately protected by a cover plate.

CE marking according to EC Declaration of Conformity for Electromagnetic Compatibility EMC - Directive 2004/108/EC. EC - Declaration of Incorporation according to the Machinery Directive 2006/42/EC - Directive 2009/125/EC (Reg.

1253/2014/EU).

Technical data:

Volumetric flow (V): m³/h Pressure increase (Δp fa): Pa Efficiency static max. (η fa): 51,7 % Efficiency total max. (ηt): 52,5 %

Rated voltage (U): 230, 1~ V Rated frequency (f): 50 Hz Rated power consumption (P N): 268 W Current consumption max. (I max.): 1,9 A Rated speed (n): 2600 min-1

Protection class motor: IP 33

Protection class terminal box: IP - Ambient temperature max. (t A): 55 °C Medium temperature max. (tM): 55 °C

Inlet sound power level (L WA5): 78 dB(A) Outlet sound power level (LWA6): 78 dB(A)

Dimensions (L x W x H): 541x541x249 mm

Weight: 8,3 kg

Schaltplan: 133375

Manufacturer:

ruck Ventilatoren GmbH Max-Planck-Str. 5

97944 Boxberg

Tel. 07930-9211300 [www.ruck.eu](http://www.ruck.eu/)

|  |  |  |
| --- | --- | --- |
| Available accessories:  DSF 280-10 | 126164 | Roof socket, flat roof size 280 |
| DSF 280-12 up to 19 |  | Sloped roof socket, size 280, slope optional in 3° increments (3-24°) |
| DSS 280-10 | 126383 | Roof socket, flat roof, sound insulated, size 280 |
| DSS 280-12 up to 19 |  | Sloped roof sound insulated socket, size 280, |
|  |  | slope optional in 3° increments (3-24°) |
| DAP 280 | 133954 | Roof adapter plate size 280 for suction side accessories (for DSS-10) |
| DVK 250 10 | 152997 | Roof - Gravity shutter size 250 |
| DAS 250 | 109413 | Roof - Inlet spigot size 250 |
| DAF 250 | 110585 | Roof - Inlet flange size 250 |
| CLIMASET 01 | 111314 | Accessories set for CON P1000, pressure hose, nipples and screws |